## Load schedule
Case | Load | Board | Qty | kW each | pf | kW | kVA | I (A)
normal | UPS-A input (IT load 500 kW at 42 % UPS loading) | MSB-A | 1 | 644.29 | 0.99 | 644.29 | 650.8 | 905.4
normal | Air-cooled chiller (VFD) | MDB-M1/M2 | 1.5 | 110 | 0.95 | 165 | 173.68 | 241.63
normal | Chilled water pump (VFD) | MDB-M1/M2 | 1.5 | 15 | 0.95 | 22.5 | 23.68 | 32.95
normal | CRAH fan (EC) | MDB-M1/M2 | 9 | 6 | 0.95 | 54 | 56.84 | 79.08
normal | Lighting and small power | LDB | 0.5 | 30 | 0.9 | 15 | 16.67 | 23.19
normal | BMS, fire and security (own UPS) | ESS-DB | 0.5 | 20 | 0.9 | 10 | 11.11 | 15.46
normal | TOTAL at MSB-A (vector sum) |  |  |  | 0.98 | 910.79 | 929.05 | 1292.5
failure | UPS-A input (IT load 1000 kW at 83 % UPS loading) | MSB-A | 1 | 1160.22 | 0.99 | 1160.22 | 1171.94 | 1630.41
failure | Air-cooled chiller (VFD) | MDB-M1/M2 | 3 | 110 | 0.95 | 330 | 347.37 | 483.26
failure | Chilled water pump (VFD) | MDB-M1/M2 | 3 | 15 | 0.95 | 45 | 47.37 | 65.9
failure | CRAH fan (EC) | MDB-M1/M2 | 18 | 6 | 0.95 | 108 | 113.68 | 158.16
failure | Lighting and small power | LDB | 1 | 30 | 0.9 | 30 | 33.33 | 46.37
failure | BMS, fire and security (own UPS) | ESS-DB | 1 | 20 | 0.9 | 20 | 22.22 | 30.92
failure | TOTAL at MSB-A (vector sum) |  |  |  | 0.98 | 1693.22 | 1728.67 | 2404.94

## Breakers (side A)
Tag | Duty | Type | Frame (A) | Ir (A) | Design current (A) | Ir loading
QA1 | Transformer TX-A incomer | ACB | 3200 | 2880 | 2782.41 | 0.97
QA2 | Generator DG-A incomer | ACB | 4000 | 3200 | 3130.21 | 0.98
QA3 | UPS-A rectifier input | ACB | 2000 | 1700 | 1630.41 | 0.96
QA4 | UPS-A static bypass input | ACB | 2000 | 1700 | 1669.45 | 0.98
QA5 | Maintenance bypass | ACB | 2000 | 1700 | 1669.45 | 0.98
QA6 | Feeder to MDB-M1 ATS (A source) | MCCB | 400 | 360 | 353.66 | 0.98
QA7 | Feeder to MDB-M2 ATS (A source) | MCCB | 400 | 360 | 353.66 | 0.98
QA8 | Feeder to LDB ATS (A source) | MCCB | 100 | 50 | 46.37 | 0.93
QA9 | Feeder to ESS-DB ATS (A source) | MCCB | 100 | 35 | 30.92 | 0.88
QA10 | UPS-A output to UPS output board | ACB | 2000 | 1700 | 1669.45 | 0.98
QA11 | UPS output board to PDU-A1 | MCCB | 400 | 360 | 347.8 | 0.97
QA12 | UPS output board to PDU-A2 | MCCB | 400 | 360 | 347.8 | 0.97
QA13 | UPS output board to PDU-A3 | MCCB | 400 | 360 | 347.8 | 0.97
QA14 | UPS output board to PDU-A4 | MCCB | 400 | 360 | 347.8 | 0.97
QA15 | UPS output board to PDU-A5 | MCCB | 400 | 360 | 347.8 | 0.97

## Busbars
Board | Rating (A) | Incomer (A) | Sum of outgoing Ir (A) | RDF (IEC 61439-1) | Diversified (A) | Icw 1 s (kA) | Form
MSB-A | 3200 | 3200 | 4205 | 0.7 | 2943.5 | 50 | Form 4b
UPS-OSB-A | 2000 | 1669.45 | 1800 | 0.8 | 1440 | 50 | Form 4b

## Summary
Item | Selected | Note
Transformer per side | 2000 kVA | 46 % normal, 86 % with B side lost
Generator per side | 2250 kVA | 77 % worst case
UPS per side | 3 x 400 kW | 42 % normal, 83 % failure
Battery per side | 10 strings x 40 blocks | 5960 W/cell needed, 173 kWh at 1 MW
PDUs per side | 5 x 250 kVA | 82 % with B side lost
Design PUE (full IT load) | 1.58 | transformer losses excluded

## Metering
Point | Meter | Purpose
TX-A incomer (QA1) | Class 0.5S multifunction, power quality | Utility energy, demand, THD
DG-A incomer (QA2) | Class 1 multifunction | Generator kWh, run hours, loading
UPS-A input (QA3) | Class 0.5S multifunction | UPS input energy, for UPS losses
UPS-A output (QA10) | Class 0.5S multifunction | Critical energy, UPS efficiency
PDU-A1..A5 incomers | Class 1 multifunction | IT energy per PDU, PUE numerator/denominator
PDU branch circuits | Branch circuit monitoring, CT per way | Rack-level current, capacity planning
MDB-M1, MDB-M2 incomers | Class 1 multifunction | Cooling energy, partial PUE
LDB, ESS-DB incomers | Class 1 multifunction | Building and life-safety energy

## BOM (both sides)
Item | Specification | Qty
Transformer | 2000 kVA, 11/0.433 kV, Dyn11, uk 6.25 %, ONAN | 2
Diesel generator | 2250 kVA prime, 415 V, with AMF controller | 2
UPS module | 400 kW double conversion, unity pf | 6
Battery block | 12 V VRLA high-rate, 10 min to 1.67 V/cell | 800
Battery string DC breaker | DC MCCB, 2P, per string | 20
Main LV switchboard | 3200 A, 50 kA 1 s, Form 4b, IEC 61439-2 | 2
UPS output switchboard | 2000 A, Form 4b | 2
ATS | 630 A, 4-pole, open transition, mech + elec interlock | 4
PDU | 250 kVA, 40-way, with branch circuit monitoring | 10
Rack PDU | 3-phase 16 A IEC 60309 (11 kVA) | 400
Branch MCB | 16 A, 4-pole, C curve, 10 kA | 400
ACB | 2000 A frame, 4-pole, Ir set 1700 A | 8
ACB | 3200 A frame, 4-pole, Ir set 2880 A | 2
ACB | 4000 A frame, 4-pole, Ir set 3200 A | 2
MCCB | 100 A frame, 4-pole, Ir set 35 A | 2
MCCB | 100 A frame, 4-pole, Ir set 50 A | 2
MCCB | 400 A frame, 4-pole, Ir set 360 A | 14
Energy meter | Class 0.5S multifunction, power quality | 2
Energy meter | Class 1 multifunction | 2
Energy meter | Class 0.5S multifunction | 2
Energy meter | Class 0.5S multifunction | 2
Energy meter | Class 1 multifunction | 10
Energy meter | Class 1 multifunction | 2
Energy meter | Class 1 multifunction | 2